UNSHIELDED TWISTED PAIR ACTIVE VIDEO RECEIVER HUB – TYPE VH3256

TECHNICAL SPECIFICATIONS					    SECURITY SYSTEM

DIVISION 16 – ELECTRICAL

SECTION 16 _ _ _  - CLOSED CIRCUIT TELEVISION (CCTV) SYSTEM

PART 2 – PRODUCTS

2.1 GENERAL

2.1.1   All equipment to be supplied under this specification shall be new and the  current

model of a standard product of an OEM of record. An OEM of record shall be

defined a a company whose main occupation is the manufacture for sale of the

equipment supplied and which:

- Maintains a factory production line for the item submitted.

- Maintains a stock of replacement parts for the item submitted..

- Maintains engineering drawings, specifications, and operating manuals for the items submitted.

- Has published and distributed descriptive literature and equipment specifications on the items of equipment submitted.

    - Specifications of equipment as set forth herein are salient and minimum requirements, unless otherwise stated and shall not be construed as limiting the overall quality, quantity or performance characteristics of items furnished.

    - Systems and components shall have been thoroughly tested and proven in actual use.

    - All systems and components shall be provided with the availability of a toll free (U.S. and Canada) technical support number from the manufacturer. The number shall provide technical assistance for either the dealer/installer or the end user at no charge

2.2  SPECIFICATIONS

    - The Twisted pair 32 channel active video receiver, shall be a NITEK Model VH3256 (or approved equivalent), and shall be capable of  receiving baseband type monochrome or color video signals over 32 separate unshielded  twisted pair (UTP) telephone cables, Category 3 or better, 24 gage or heavier up to a maximum cable length of 3,000 feet (900 meters), when connected to any

NITEK Passive Video Transceiver (or approved equivalent) at the opposite end

of the UTP.

    - The Twisted pair active video receiver hub, shall be capable of receiving baseband  type monochrome or color video signals over cables as specified in

Paragraph 2.2.1 to a maximum cable length of 6,000 feet (1,800 meters), when

connected to a NITEK Model TT560 active  Video Transmitter (or approved equivalent) at the opposite end of the UTP.

    - The active receiver hub shall consist of a NITEK model VH3200 Powered Card Cage, or approved equivalent and four NITEK model TR560x8 plug-in cards, or approved equivalent.

    - Receiving video signals, as described in paragraph 2.2.1 shall mean that the active video receiver shall be capable of delivering a monochrome or color video signal of 525 lines at the maximum specified distances.

UNSHIELDED TWISTED PAIR ACTIVE VIDEO RECEIVER HUB – VH3256

TECHNICAL SPECIFICATIONS					    SECURITY SYSTEM

DIVISION 16 – ELECTRICAL

SECTION 16 _ _ _  - CLOSED CIRCUIT TELEVISION (CCTV) SYSTEM

PART 2 – PRODUCTS (continued)

  - SPECIFICATIONS (continued)

    - The active receiver hub shall be provided with a power pack capable of providing 24 VAC at 450 ma. The power pack shall have provisions to plug directly into an AC wall outlet and shall provide two wires (2 foot minimum in length) to connect to the receiver power terminals.

    - The active receiver hub shall have a snap-on removable front panel. Front panel

removal shall provide access to 32 dual in-line (DIP) switches, one for each

video receiver channel. The switches shall provide frequency equalization and

compensation for varying cable lengths from 100 to 1,500 feet, when a NITEK

    - passive transmitter (or approved equivalent) is used and from 500 to 6,000 feet when a NITEK TT560 active transmitter is used. The effect of the frequency compensation shall be to both equalize and to amplify the video signal thereby providing loss compensation for video as cable length is increased.

    - Each channel of the active receiver hub shall be capable of equalizing a color video signal of NTSC standard 525 lines or PAL standard 625 lines and shall deliver a baseband video signal capable of driving a 75 ohm impedance load.

.

2.2.6     The active receiver hub shall have built-in transient protection.

2.2.7     Video connection to the active receiver hub shall be by means of 32 BNC type

female connector. connection to UTP cable shall be by means of two sixteen

circuit terminal blocks, with 2 circuits for each pair. Each circuit shall provide a

slotted head screw for securing the wire. The screw terminals shall be plated with

a rust preventive material to prevent corrosion.

    - The active receiver hub shall also operate as specified in paragraph 2.2.1

when used as a receiver for any commercially available UTP equipped

camera, camera enclosure and/or dome in which a NITEK Model VB24 (or

approved equivalent) is installed as a transmitter device.

2.2.9   The active receiver hub shall operate within specifications without causing

interference or interfering with any other base band video, communication, data

and/or other low-voltage signals operating in multi-twisted pair UTP cables as

specified in paragraph 2.2.1 or 2.2.2.

2.2.10 The active receiver hub shall be covered by a Limited Two Year Warranty.

UNSHIELDED TWISTED PAIR ACTIVE VIDEO RECEIVER HUB  – VH3256

TECHNICAL SPECIFICATIONS					    SECURITY SYSTEM

DIVISION 16 – ELECTRICAL

SECTION 16 _ _ _  - CLOSED CIRCUIT TELEVISION (CCTV) SYSTEM

PART 2 – PRODUCTS (continued)

2.3  PERFORMANCE SPECIFICATIONS

    - The active receiver hub unit shall meet or exceed the following performance specifications:

- With a symmetrical and balanced composite input from the transmitter unit and using cables as specified in paragraph 2.2.1, at a cable length of 1,500 feet, the output shall be a 1 Vpp composite video signal into 75 ohms.

- The  receiver unit shall be capable of receiving RS170, NTSC, PAL, SECAM and CCIR video formats (color or monochrome).

- Operating frequency range: DC to 10 MHz.

- Common mode rejection to be > 70 dB.

- Voltage requirements: 24 VAC Power Supply provided.

H .Temperature: System must operate in an ambient temperature of –40

Degrees C to +85 degrees C, 0 to 98% non-condensing.